| New Options |  |  |
| --- | --- | --- |
| GEMC-KEYSWKIT Keyswitch Kit |  | - To be used in cases where it is required that a keyswitch be used to unlock the fire keypad. The GEMC-KEYSWKIT consists of an easy-to-install keypad / keyswitch mounting box that allows codeless locking and unlocking of the Napco GEM-FK1 Fire alarm keypad. The GEMC-KEYSWKIT is designed to be mounted to a one, two or three-gang electrical box, or to a hollow wall using mounting hardware appropriate for the mounting surface. The keyswitch is wired into one of two existing GEMC-FK1 keypad inputs; when the key is inserted and rotated, the keyswitch closes, triggering a keypad command to the control panel to unlock that keypad. - This feature may be configured to allow either a maintained or momentary keyswitch closure to unlock the keypad for a 15 minute period OR a maintained keyswitch closure which will unlock the keypad when opened will lock the keypad when closed |
| GEMC-LOCK-CAT30 Key-Alike |  | - To be used in cases where it is required that the same key used to reset the pull stations also be used to unlock the control panel enclosure. Simply replace the standard enclosure lock with the GEMC-LOCK-CAT30 to "key alike" the pull station and enclosure lock. Note - the GEMC-KEYSWKIT, above is also keyed to CAT 30, allowing one key to unlock the keypad, reset the pull stations and open the GEMC control panel enclosure. |
| FN-CTM City Tie Module |  | - The FN-CTM is a City Tie Module used to connect the GEMC Fire Alarm Control Panel to a Local Energy type City Tie Monitoring circuit. The FN-CTM City Tie Module circuit provides the power necessary to trip the Master Box Trip Coil when the Fire Alarm Control Panel goes into alarm. The City Tie Circuit is capable of providing 1A for 0.5 seconds to operate the Master Box Trip Coil. The wiring is supervised to the Master Box by placing the EOL resistor device on the terminals of the FN-CTM City Tie Module. |